## Cover
BESS SITING DATA COMPENDIUM
Suffolk & Middlesex Counties, Massachusetts
Project: Next-Generation Energy Siting Tool — MassDOER × TPS Fellowship
Compiled: April 2026 ¦ Version 1.0 ¦ Scope: Suffolk & Middlesex Counties, MA
ISO-NE Zones: NEMA (Northeast MA/Boston) and SENE (Southern New England)
State Storage Goal: 5,000 MW by July 31, 2030 (MA 2024 Climate Act, Chapter 239)
SHEETS IN THIS WORKBOOK
1. Municipalities — Composite siting scores, demographics, grid & zoning data for all 13 municipalities
2. ISO-NE Market — LMP pricing data, Forward Capacity Auction results, system load forecasts
3. Hosting Capacity — Eversource & National Grid hosting capacity details, DOE Atlas overview
4. Costs & Revenue — NREL cost projections, 4-hr BESS revenue stack, ITC stacking, interconnection costs
5. Project Pipeline — Active BESS projects in Suffolk & Middlesex; 83E procurement schedule
6. EJ & Demographics — EJ population data, energy burden, CIA framework for all municipalities
7. Zoning & Law — DOER Model Bylaw tiers, EFSB jurisdiction, municipal zoning status
8. Sources — Full citations for all 26+ data sources used in this compendium
KEY HEADLINE FIGURES
2030 MW Storage Goal: 5,000 MW (MA statutory mandate, Chapter 239)
Installed Statewide: 644 MWh (as of early 2025)
Permitted in Suffolk + Middlesex: ~1,285 MW / ~5,140 MWh = 25.7% of 5,000 MW goal
NEMA Summer 2025 Peak LMP: $53.31/MWh
June 24, 2025 Scarcity Event Peak: ~$1,600/MWh
4-hr BESS Revenue Stack (NEMA zone): $90–$170+/kW-year
Maximum Federal ITC (stackable): Up to 70% (EJ brownfield projects)

## Municipalities
Municipality Siting Scores & Profiles — Suffolk & Middlesex Counties, MA
Source: MassGIS OEJE 2020, Eversource, National Grid, ISO-NE, DOER Model Bylaw, MassDOER ¦ April 2026
ID | Municipality | County | Population (2020) | Median HH Income ($) | % Minority | % EJ Designated | CIA Classification | EJ Score (/25) | Grid Score (/25) | Zoning Score (/25) | Physical Score (/25) | Revenue Score (/25) | Composite Score (/125) | Grid Hosting Capacity | Interconnect Risk | Utility | Max Feasible MW | Best Duration | Permitting Timeline | Setback (ft) | Zoning Class | Brownfield Site | Active Project | Energy Burden (% Income) | Asthma Rate | LMP Premium vs Hub (%) | ISO-NE Zone
everett | Everett | Middlesex | 49075 | 79658 | 62 | 100 | Very High | 25 | 25 | 22 | 24 | 23 | 119 | Very High | Very Low | Eversource | 700 | 8hr | 7–9 mo | 50 | I-2 Heavy Industrial | Yes | 700 MW Trimount ESS (EFSB approved Feb 2025) | 7.8 | High | 1.4 | SENE
chelsea | Chelsea | Suffolk | 40787 | 62000 | 80 | 100 | Very High | 25 | 23 | 20 | 21 | 24 | 113 | High | Low | Eversource | 12 | 4hr | 8–10 mo | 50 | I-1/I-2 Industrial | Yes | 250 MW Energizar (permitted Oct 2024) | 8.1 | 2× state avg | 1.4 | SENE
lowell | Lowell | Middlesex | 115554 | 76000 | 56 | 96 | High | 22 | 19 | 22 | 23 | 19 | 105 | High | Low-Med | National Grid | 16 | 4hr | 9–11 mo | 75 | Industrial / Mill Reuse | Yes | None confirmed | 7.4 | High | 1.3 | NEMA
eastboston | East Boston | Suffolk | 44000 | 55000 | 71 | 100 | Very High | 24 | 21 | 16 | 18 | 25 | 104 | Medium | Medium | Eversource | 7 | 2hr | 10–13 mo | 60 | IA/NB Commercial | No | None confirmed | 9.2 | 2× state avg | 1.5 | SENE
malden | Malden | Middlesex | 66263 | 98000 | 58 | 100 | High | 22 | 20 | 18 | 20 | 21 | 101 | High | Low | Eversource | 15 | 4hr | 9–11 mo | 50 | Industrial/Commercial | No | None | 6.1 | Elevated | 1.3 | SENE
framingham | Framingham | Middlesex | 72362 | 88000 | 40 | 87 | High | 20 | 18 | 19 | 21 | 18 | 96 | High | Low-Med | National Grid | 18 | 4hr | 10–12 mo | 75 | Industrial (Route 9 Corridor) | No | None | 5.6 | Elevated | 1.2 | NEMA
revere | Revere | Suffolk | 62186 | 87000 | 50 | 100 | High | 21 | 19 | 14 | 17 | 22 | 93 | Medium | Medium | Eversource | 5 | 2hr | 11–14 mo | 75 | Hwy Business (amendment proposed) | No | Zoning amendment in progress (Sept 2025) | 6.4 | Elevated | 1.2 | SENE
boston | Boston | Suffolk | 675647 | 82000 | 53 | 84 | High | 18 | 20 | 15 | 14 | 24 | 91 | Medium | Med-High | Eversource | 10 | 4hr | 12–15 mo | 60 | No BESS-specific zoning | Yes | 185 MW Electric Ave (Brighton, in dev) | 5.8 | Elevated | 1.3 | SENE
waltham | Waltham | Middlesex | 62227 | 95000 | 37 | 74 | Moderate | 17 | 17 | 16 | 16 | 19 | 85 | Medium | Medium | Eversource | 8 | 4hr | 12–14 mo | 75 | Industrial Zones | No | None | 4.9 | Average | 1.2 | SENE
cambridge | Cambridge | Middlesex | 118403 | 105000 | 40 | 95 | High | 20 | 18 | 13 | 10 | 23 | 84 | Medium | Medium | Eversource | 6 | 2hr | 13–16 mo | 75 | Business/Mixed-Use | No | None | 4.8 | Average | 1.4 | SENE
somerville | Somerville | Middlesex | 81045 | 95000 | 35 | 73 | Moderate | 17 | 17 | 14 | 12 | 21 | 81 | Medium | Medium | Eversource | 5 | 2hr | 13–16 mo | 75 | Commercial/Mixed-Use | No | None | 5.2 | Average | 1.3 | SENE
medford | Medford | Middlesex | 59659 | 122000 | 33 | 73 | Moderate | 16 | 16 | 15 | 15 | 19 | 81 | Medium | Medium | Eversource | 6 | 4hr | 12–15 mo | 75 | Industrial/Commercial | No | None | 4.3 | Average | 1.2 | SENE
winthrop | Winthrop | Suffolk | 19316 | 85000 | 20 | 44 | Moderate | 10 | 12 | 10 | 8 | 16 | 56 | Low | High | Eversource | 2 | 2hr | 14–18 mo | 100 | Residential-dominant | No | None | 4.2 | Average | 1.1 | SENE

## ISO-NE Market
ISO-NE Grid & Market Data — NEMA/SENE Zones
Sources: ISO-NE Annual Markets Report 2024, ISO-NE EMM Report, FCA Results, felpower.com ¦ April 2026
A. LOCATIONAL MARGINAL PRICING (LMP)
Metric | Value / Price | Period | Source | Notes
Hub Day-Ahead LMP 2024 | $41.47 | 2024 | ISO-NE 2024 Annual Markets Report
Hub Real-Time LMP 2024 | $39.50 | 2024 | ISO-NE 2024 Annual Markets Report
NEMA Day-Ahead LMP 2024 (est.) | $42.09 | 2024 | Calculated at ~1.5% above Hub
Hub Winter 2024 | $48.66 | Winter 2024 | ISO-NE QMR
Hub Summer 2024 | $39.03 | Summer 2024 | ISO-NE QMR
NEMA Summer 2025 | $53.31 | Summer 2025 | ISO-NE QMR
Peak Event (June 24, 2025) | $1,600 | June 24 2025 | felpower.com; ISO-NE
Pay-for-Performance Penalty | >$9,300 | Effective June 2025 | ISO-NE
B. FORWARD CAPACITY AUCTION (FCA) RESULTS — SENE ZONE
Auction | Capacity Period | SENE ($/kW-month) | Rest-of-Pool ($/kW-month) | Key Notes
FCA 14 | 2023–2024 | 2.001 | 2.001 | All zones uniform
FCA 15 | 2024–2025 | 3.98 | 2.611 | SENE import-constrained; 52% premium; ~600 MW storage cleared
FCA 16 | 2025–2026 | 2.639 | 2.591 | ~700 MW storage cleared
FCA 17 | 2026–2027 | 2.59 | 2.59 | All zones uniform
FCA 18 | 2027–2028 | 3.58 | 3.58 | 38% increase from FCA 17; ~795 MW new solar+storage
C. SYSTEM LOAD FORECASTS
Metric | Value | Period | Source | Notes
Average Hourly Load | 13,924 MW | 2024 | ISO-NE 2024 Annual Markets Report
Annual Energy Served | 117,744 GWh | 2025 | ISO-NE Key Stats
NEMA Zone Share of Load | ~25–28% (~5,000–6,500 MW peak) | Historical | ISO-NE CELT Report
Summer 50/50 Net Peak Forecast | 26,897 MW | 2034 | 2025 CELT Report
Winter Net Peak Forecast (normal) | 26,020 MW | 2034 | 2025 CELT Report
Winter Net Peak Forecast (cold) | 28,714 MW | 2034 | 2025 CELT Report
Winter Peak Growth Rate | 2.9%/year | 2025–2034 | 2025 CELT Report | Projected winter-peaking by 2032
All-Time Summer Peak | 28,130 MW | Aug 2, 2006 | ISO-NE Key Stats
June 24 2025 Scarcity Peak | 26,135 MW | June 24 2025 | felpower.com; ISO-NE | Highest since 2013; $1,600/MWh peak LMP
D. INTERCONNECTION QUEUE
Metric | Value | Date | Source | Notes
Total Queue Capacity | ~14,000 MW | January 2026 | ISO-NE; Energy-Storage.News | Down from ~38,000 MW in 2023 after FERC Order 2023 changes
Storage Share of Queue | ~45–46% by project count | January 2026 | ISO-NE
Estimated Storage in Queue | ~6,300–6,400 MW | January 2026 | Calculated
Transitional Cluster Study Projects | 26 total (21 battery storage) | October 2025 | isonewswire.com
Cluster Study Combined Capacity | ~8 GW | October 2025 | Utility Dive | Most located in Massachusetts
Mean Interconnection Cost (storage) | $230/kW | 2018–2021 studies | LBNL June 2023
Median Interconnection Cost | $148/kW | 2018–2021 studies | LBNL June 2023

## Hosting Capacity
Grid Hosting Capacity & Interconnection — MA Utilities
Sources: Eversource Hosting Capacity Map, National Grid SDP, U.S. DOE Atlas, Eversource DER Project Costs ¦ April 2026
A. EVERSOURCE MASSACHUSETTS
Item | Value / URL | Date | Source | Notes
Service Area | Suffolk County (all), most of Middlesex County
Interactive Map | https://www.eversource.com/residential/about/doing-business-with-us/interconnections/massachusetts/hosting-capacity-map
Grid Connection Navigator (envelio) | https://navigator.eversource.envelio.com/ (launched Dec 2025)
ORNL Bulk Data | https://openenergyhub.ornl.gov/explore/dataset/dghosting_adminvw_dg_hosting_ced_ema_st/
MA Territory Pipeline (Dec 31 2024) | ~4,546 MWh / 1,244 MW | Dec 31 2024 | EDC quarterly reports | Installed or in pipeline
Data Access Note | Circuit-specific MW values require interactive tool queries; no bulk static extraction
B. NATIONAL GRID MASSACHUSETTS (MIDDLESEX COUNTY)
Item | Value / URL | Date | Source | Notes
Service Area | Lowell, Dracut, Tewksbury, Chelmsford, Billerica, Framingham
Portal | https://systemdataportal.nationalgrid.com/MA/ |  |  | ArcGIS-based portal
Methodology | CymeDist modeling with EPRI DRIVE tool |  |  | Nodal hosting capacity analysis
MA Territory Pipeline (Dec 31 2024) | ~8,826 MWh / 1,059 MW | Dec 31 2024 | EDC quarterly reports | Installed or in pipeline
FERC-Approved Wholesale Tariff | F-1 Rate: $20.94/mo access + $0.51/kW contract demand + $7.28/kW as-used peak | March 2024 | FERC | For standalone storage on distribution participating in wholesale markets
C. EVERSOURCE DER INTERCONNECTION UPGRADE COSTS (MA)
Upgrade Category | Cost Low ($) | Cost High ($) | Unit | Source
Overhead Point of Interconnection | $400,000 | $400,000 |  | Eversource MA DER Project Costs (2021–2022)
Underground POI (>500 kW) | $650,000 | $650,000 |  | Eversource MA DER Project Costs (2021–2022)
Conductor Reconductoring | $1,000,000 | $1,300,000 | Per mile | Eversource MA DER Project Costs (2021–2022)
Express Feeder Extension | $1,000,000 | $1,300,000 | Per mile | Eversource MA DER Project Costs (2021–2022)
Underground Cable Replacement | $1,900,000 | $9,500,000 | Per mile | Eversource MA DER Project Costs (2021–2022)
Substation Transformer Upgrade (115–23kV) | $4,000,000 | $4,000,000 | 60–65 MVA | Eversource MA DER Project Costs (2021–2022)
New Feeder Position/Getaway | $2,000,000 | $2,000,000 |  | Eversource MA DER Project Costs (2021–2022)
Pad-Mounted Switchgear | $200,000 | $250,000 |  | Eversource MA DER Project Costs (2021–2022)
Recloser Installation | $100,000 | $150,000 |  | Eversource MA DER Project Costs (2021–2022)
DTT Installation | $500,000 | $500,000 |  | Eversource MA DER Project Costs (2021–2022)
D. MUNICIPALITY HOSTING CAPACITY SUMMARY
Municipality | County | Utility | Hosting Capacity | Interconnect Risk
Everett | Middlesex | Eversource | Very High | Very Low
Chelsea | Suffolk | Eversource | High | Low
Lowell | Middlesex | National Grid | High | Low-Med
East Boston | Suffolk | Eversource | Medium | Medium
Malden | Middlesex | Eversource | High | Low
Framingham | Middlesex | National Grid | High | Low-Med
Revere | Suffolk | Eversource | Medium | Medium
Boston | Suffolk | Eversource | Medium | Med-High
Waltham | Middlesex | Eversource | Medium | Medium
Cambridge | Middlesex | Eversource | Medium | Medium
Somerville | Middlesex | Eversource | Medium | Medium
Medford | Middlesex | Eversource | Medium | Medium
Winthrop | Suffolk | Eversource | Low | High

## Costs & Revenue
BESS Costs & Revenue Modeling Data
Sources: NREL 2025 Cost Projections (DOI:10.2172/2583471), NREL 2024 ATB, ISO-NE, MassDOER CPS, SMART Program ¦ April 2026
A. NREL BATTERY STORAGE INSTALLED COST PROJECTIONS — 4-HR UTILITY-SCALE LFP ($/kWh)
Year | Low ($/kWh) | Mid ($/kWh) | Change from 2024 Low (%) | Notes
2024 | $334 | $334 | Baseline | Q1 2024 benchmark; 4-hr utility-scale LFP
2026 | $255 | $308 | -24%
2028 | $210 | $275 | -37%
2030 | $177 | $243 | -47%
2035 | $150 | $245 | -55%
B. 4-HOUR BESS REVENUE STACK — ISO-NE NEMA/SENE ZONE
Revenue Stream | Low ($/kW-yr) | High ($/kW-yr) | Mid ($/kW-yr) | Source / Notes
Energy Arbitrage (LMP spread) | $40 | $80 | $60 | NREL 2021 median $63/kW for 6hr; ISO-NE historical LMP
Forward Capacity Market (FCM) | $31 | $48 | $39 | FCA 15–18 clearing prices; SENE zone
Clean Peak Energy Certificates (CPS) | $15 | $65 | $40 | ACP $65/MWh (2026–2032); multipliers up to 25×
Ancillary Services | $2 | $10 | $6 | ISO-NE regulation market
SMART Storage Adder | $10 | $25 | $17 | SMART 2.0/3.0 adders $0.025–$0.077/kWh
TOTAL | $90 | $170+ | $130 | All streams combined
C. FEDERAL TAX CREDITS — ITC STACKING (ONE BIG BEAUTIFUL BILL ACT, JULY 2025)
Credit Component | Rate | Cumulative Rate | Eligible For | Notes
Base ITC (Section 48E) | 6% | 6% | All BESS projects (Section 48E) | Without prevailing wage compliance
With Prevailing Wage & Apprenticeship | 30% | 30% | Projects >1 MW with certified prevailing wage/apprenticeship compliance | Required for projects >1 MW
+ Domestic Content Bonus | 40% total | 40% | US-produced steel, iron, and manufactured product content | US-produced steel, iron, manufactured products
+ Energy Community Bonus | 50% total | 50% | Brownfields, closed coal plants, high-unemployment fossil fuel communities | Brownfields, closed coal, high-unemployment fossil fuel areas
+ Low-Income Community Bonus | Up to 70% total | Up to 70% | Low-income census tracts or projects serving low-income residents | Low-income census tract or serving low-income residents

## Project Pipeline
Active BESS Project Pipeline — Suffolk & Middlesex Counties
Sources: Mass.gov Everett Battery Project, Chelsea Record, Boston.gov, pv magazine USA, Energy-Storage.News ¦ April 2026
A. CONFIRMED / SELECTED PROJECTS
Project | Municipality | County | MW | MWh | Developer | Status | Est. Cost | Key Details
Trimount ESS | Everett | Middlesex | 700 | 2800 | Jupiter Power (BlackRock) | EFSB approved Feb 2025; 83E Rd1 Selected | $500M–$1B+ | Former ExxonMobil terminal, 20.75 ac; Hithium LFP; defers $2.2B transmission upgrades
Energizar | Chelsea | Suffolk | 250 | 1000 | Flatiron Energy | ZBA permitted Oct 2024; 83E Rd1 Selected | ~$120M est. | 284 Eastern Ave, adj. Eversource substation; $1.5M/yr PILOT + $550K HCA; Q2 2027 ops target
Electric Ave | Brighton (Boston) | Suffolk | 185 | 740 | Flatiron/CME/Hecate | In Development; ISO-NE interconnect ≥ June 2027 | Est. $90M+ | Indoor BESS; community opposition noted
River Mill | Tyngsborough | Middlesex | 150 | 600 | Rhynland Energy | 83E Round 1 Selected; details TBD | Undisclosed | Merrimack River corridor; capacity unconfirmed publicly
TOTAL |  |  | ~1,285 | ~5,140
B. SECTION 83E LONG-TERM PROCUREMENT SCHEDULE
Round | Date | MW Awarded / Planned | Notes
Round 1 | December 2025 | 1,268 MW (4 projects from 13 bids) | 20-year CPEC contracts
Round 2 | 2026 | ~1,200 MW planned | Mid-duration focus (4–10 hr)
Round 3 | 2027 | ~1,200 MW planned | Long-duration (10–24 hr)
Round 4 | 2028 | ~1,300 MW planned | Multi-day (>24 hr) if feasible
C. STATEWIDE STORAGE GOAL PROGRESS
Metric | Value | Date | Source
Statutory Target | 5,000 MW | By July 31, 2030 | MA 2024 Climate Act Chapter 239
Installed Statewide | 644 MWh | Early 2025 | Mass.gov ESI Goals
Development Pipeline Statewide | 12,932 MWh | Early 2025 | TomorrowIQ; Energy-Storage.News
Eversource MA Territory Pipeline | ~4,546 MWh / 1,244 MW | Dec 31, 2024 | EDC quarterly reports
National Grid MA Territory Pipeline | ~8,826 MWh / 1,059 MW | Dec 31, 2024 | EDC quarterly reports
Permitted in Suffolk + Middlesex | ~1,285 MW / ~5,140 MWh | April 2026 | This analysis
% of 5,000 MW Goal from S+M | 25.7% | April 2026 | Calculated

## EJ & Demographics
Environmental Justice & Demographic Data — All 13 Municipalities
Sources: MassGIS 2020 EJ Population Layer, MA Household Economic Burden Index, DOE LEAD Tool, MA DPH ¦ April 2026
A. EJ DESIGNATION & HEALTH BURDEN BY MUNICIPALITY
Municipality | County | Population (2020) | Median HH Income ($) | % Minority | % EJ Designated | CIA Classification | Energy Burden (% Income)
East Boston | Suffolk | 44000 | 55000 | 71 | 100 | Very High | 9.2
Chelsea | Suffolk | 40787 | 62000 | 80 | 100 | Very High | 8.1
Everett | Middlesex | 49075 | 79658 | 62 | 100 | Very High | 7.8
Lowell | Middlesex | 115554 | 76000 | 56 | 96 | High | 7.4
Revere | Suffolk | 62186 | 87000 | 50 | 100 | High | 6.4
Malden | Middlesex | 66263 | 98000 | 58 | 100 | High | 6.1
Boston | Suffolk | 675647 | 82000 | 53 | 84 | High | 5.8
Framingham | Middlesex | 72362 | 88000 | 40 | 87 | High | 5.6
Somerville | Middlesex | 81045 | 95000 | 35 | 73 | Moderate | 5.2
Waltham | Middlesex | 62227 | 95000 | 37 | 74 | Moderate | 4.9
Cambridge | Middlesex | 118403 | 105000 | 40 | 95 | High | 4.8
Medford | Middlesex | 59659 | 122000 | 33 | 73 | Moderate | 4.3
Winthrop | Suffolk | 19316 | 85000 | 20 | 44 | Moderate | 4.2
B. SUFFOLK COUNTY EJ BLOCK GROUP DATA
Municipality | EJ Block Groups | Total Block Groups | % EJ | Pop in EJ BGs | % Pop in EJ | Key EJ Triggers
Boston | 462 | 581 | 79.5% | 571,192 | 84.4% | Minority, Income, English Isolation
Chelsea | 36 | 37 | 97.3% | 40,787 | 100% | All three criteria
Revere | 44 | 45 | 97.8% | 62,179 | 100% | All three criteria
Winthrop | 7 | 18 | 38.9% | 8,480 | 43.9% | Minority, Income
County Total | 549 | 681 | 80.6% | 682,638 | 85.5%
C. MA EJ DESIGNATION CRITERIA (MASSGIS 2020)
# | Criterion | Threshold | Type
1 | Minority population | ≥40% of census block group | Mandatory trigger
2 | Median household income | ≤65% of statewide median (~$54,850) | Mandatory trigger
3 | English proficiency | ≥25% of households lack English proficiency | Mandatory trigger
4 | Combined minority + income | Minorities ≥25% AND municipal median income ≤150% statewide median | Mandatory trigger
D. CUMULATIVE IMPACT ANALYSIS (CIA) FRAMEWORK
Item | Value / Description | Effective Date | Source
CIA Effective Date | July 1, 2024 | July 1, 2024 | Chapter 8 of the Acts of 2021
Number of Indicators | 33 environmental, health, and socioeconomic factors |  | OEJE
BESS CIA Regulations | 980 CMR 15.00 — issued January 23, 2026 | January 23, 2026 | OEJE
Tool in Development | MassEnviroScreen (analogous to California's CalEnviroScreen) | TBD | OEJE
National Grid Low-Income Discount | Up to 71% discount (tiered, approved Oct 2024) | October 2024 | WBUR
Eversource Low-Income Discount | 42% flat discount | Ongoing | Mass.gov
Chelsea Asthma Note | 5th highest asthma hospitalization rate in MA; ~2× statewide average |  | MA DPH

## Zoning & Law
Zoning Regulations & Legal Framework — Suffolk & Middlesex Counties
Sources: DOER Model Bylaw (Oct 2025), MA 2024 Climate Act, Pierce Atwood, Foley Hoag, Municipal Zoning Codes ¦ April 2026
A. DOER MODEL BESS BYLAW — THREE-TIER FRAMEWORK (OCTOBER 6, 2025)
Tier | Capacity Range | Industrial Zone | Commercial Zone | Residential Zone | Notes
Tier 1 | < 250 kWh | By-Right | By-Right | By-Right | No permit required
Tier 2 | 250 kWh – <10 MWh | By-Right | Site Plan Review | Special Permit
Tier 3 | 10 MWh – <100 MWh | Site Plan Review | Special Permit | Special Permit
≥100 MWh | ≥100 MWh | EFSB Sole Jurisdiction | EFSB Sole Jurisdiction | EFSB Sole Jurisdiction | Effective July 1, 2026; 15-month deadline; auto-approval if missed
B. KEY LEGAL REGULATIONS AND PRECEDENTS
Law / Regulation | Description | Effective Date | Source | Impact
2024 Climate Act (Chapter 239) | EFSB sole jurisdiction ≥100 MWh; 5,000 MW mandate; 3-tier procurement | Nov 20, 2024 (signed) | MA Legislature | Transforms permitting landscape statewide
EFSB Sole Jurisdiction | Single consolidated permit; 15-month deadline; replaces all local permits | July 1, 2026 | Chapter 239 | Eliminates municipal veto for large projects
Local Consolidated Permitting | 12-month deadline for <100 MWh local opt-in | October 1, 2026 | Chapter 239 | Provides faster local permitting path
DOER Model BESS Bylaw | 3-tier by-right/SPR/SP framework for municipalities | October 6, 2025 | MassDOER | Template for consistent local regulation
Dover Amendment (M.G.L. c.40A §3) | Protects standalone BESS from arbitrary municipal prohibition | Ongoing | MA Law | Strong developer protection
Duxbury Energy Storage v. Duxbury ZBA | Dover Amendment upheld; standalone BESS protected | June 2025 | MA Land Court | Confirms legal protections for developers
225 CMR 29.00 | DOER implementing regulations for small clean energy facility siting | Feb 27, 2026 | MassDOER | Clarifies small project pathway
527 CMR 1.00 / NFPA 855 | Fire safety code for Li-ion BESS >20 kWh; UL 9540 required | Ongoing | MA Fire Marshal | Mandatory compliance at all scales
C. MUNICIPALITY ZONING STATUS
Municipality | County | Utility | BESS Zoning / Notes | Setback (ft) | Permitting Timeline
Everett | Middlesex | Eversource | I-2 Heavy Industrial | 50 ft | 7–9 mo
Chelsea | Suffolk | Eversource | I-1/I-2 Industrial | 50 ft | 8–10 mo
Lowell | Middlesex | National Grid | Industrial / Mill Reuse | 75 ft | 9–11 mo
East Boston | Suffolk | Eversource | IA/NB Commercial | 60 ft | 10–13 mo
Malden | Middlesex | Eversource | Industrial/Commercial | 50 ft | 9–11 mo
Framingham | Middlesex | National Grid | Industrial (Route 9 Corridor) | 75 ft | 10–12 mo
Revere | Suffolk | Eversource | Hwy Business (amendment proposed) | 75 ft | 11–14 mo
Boston | Suffolk | Eversource | No BESS-specific zoning | 60 ft | 12–15 mo
Waltham | Middlesex | Eversource | Industrial Zones | 75 ft | 12–14 mo
Cambridge | Middlesex | Eversource | Business/Mixed-Use | 75 ft | 13–16 mo
Somerville | Middlesex | Eversource | Commercial/Mixed-Use | 75 ft | 13–16 mo
Medford | Middlesex | Eversource | Industrial/Commercial | 75 ft | 12–15 mo
Winthrop | Suffolk | Eversource | Residential-dominant | 100 ft | 14–18 mo
D. AGO-REJECTED MUNICIPAL MORATORIUMS (REFERENCE)
Municipality | Year | Outcome | Notes
Carver | 2022 | Rejected by AG | First major rejection
Wendell | 2022–2025 | Rejected by AG | 4-year Home Rule battle; repeatedly rejected
Shutesbury | 2024 | Rejected by AG
Sherborn | 2024 | Rejected by AG
Blandford | 2026 | Rejected by AG | Most recent rejection
Suffolk County | N/A | NO MORATORIUMS | Zero bans or moratoriums in Suffolk County
Middlesex County | N/A | NO MORATORIUMS | Zero bans or moratoriums in Middlesex County

## Sources
Data Sources — Full Citation List
All sources used in the BESS Siting Data Compendium for Suffolk & Middlesex Counties, MA ¦ April 2026
Source Title | Organization | URL
ISO-NE 2024 Annual Markets Report | ISO-NE | https://www.iso-ne.com/static-assets/documents/100023/2024-annual-markets-report.pdf
ISO-NE 2024 EMM Report | ISO-NE | https://www.iso-ne.com/static-assets/documents/100025/iso-ne-2024-emm-report-final.pdf
ISO-NE NEMA Zone Load Data | ISO-NE | https://www.iso-ne.com/isoexpress/web/reports/load-and-demand/-/tree/whlsecost-hourly-nemassbost
ISO-NE SEMA Zone Load Data | ISO-NE | https://www.iso-ne.com/isoexpress/web/reports/load-and-demand/-/tree/whlsecost-hourly-semass
ISO-NE FCA Results | ISO Newswire | https://isonewswire.com
Eversource Hosting Capacity Map MA | Eversource | https://www.eversource.com/residential/about/doing-business-with-us/interconnections/massachusetts/hosting-capacity-map
Eversource DER Project Costs MA | Eversource | https://www.eversource.com/content/wma/residential/about/doing-business-with-us/builders-contractors/interconnections/massachusetts/distributed-energy-resources-project-costs
National Grid MA System Data Portal | National Grid | https://systemdataportal.nationalgrid.com/MA/
ORNL OpenEnergyHub Eversource DG Hosting Capacity | ORNL | https://openenergyhub.ornl.gov/explore/dataset/dghosting_adminvw_dg_hosting_ced_ema_st/
U.S. DOE Atlas of Hosting Capacity Maps | DOE | https://www.energy.gov/cmei/us-atlas-electric-distribution-system-hosting-capacity-maps
MassGIS 2020 EJ Population Data | MassGIS | https://www.mass.gov/info-details/massgis-data-2020-environmental-justice-populations
MA Cumulative Impact Analysis | Mass.gov | https://www.mass.gov/info-details/cumulative-impact-analysis
MA Household Economic Burden Index | Mass.gov | https://www.mass.gov/files/documents/2023/04/25/MECO%20Utility%20Index_Dec%202022_final.pdf
NREL 2025 Battery Cost Projections | NREL | https://docs.nrel.gov/docs/fy25osti/93281.pdf
NREL 2024 Annual Technology Baseline | NREL | https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage
DOER Draft BESS Model Bylaw Oct 2025 | MassDOER | https://www.mass.gov/doc/doer-draft-battery-energy-storage-systems-bess-model-bylaw/download
Mass.gov ESI Goals & Storage Target | Mass.gov | https://www.mass.gov/info-details/esi-goals-storage-target
Mass.gov Everett Battery Project | Mass.gov | https://www.mass.gov/info-details/everett-battery-project
Pierce Atwood — Chapter 239 Analysis | Pierce Atwood LLP | https://www.pierceatwood.com/alerts/breaking-massachusetts-passes-clean-energy-bill-streamlining-permitting-process-battery
Foley Hoag — AGO Moratorium Rejections | Foley Hoag LLP | https://foleyhoag.com/news-and-insights/blogs/energy-and-climate-counsel/2026/march/massachusetts-ago-rejects-yet-another-municipal-solar-and-battery-storage-moratorium/
Chelsea Record — Energizar ZBA Approval | Chelsea Record | http://chelsearecord.com/2024/10/17/zba-okays-approvals-for-battery-storage-facility/
pv magazine USA — 83E Round 1 Awards | pv magazine USA | https://pv-magazine-usa.com/2025/12/23/massachusetts-awards-1-3-gw-in-landmark-energy-storage-tender/
Energy-Storage.News — MA 5,000 MW | Energy-Storage.News | https://www.energy-storage.news/massachusetts-moves-toward-goal-of-5000mw-of-bess-by-2030/
felpower.com — System Peak 2025 | felpower | https://felpower.com/annual-system-peak-summary-2025-september-newsletter/
National Zoning Atlas MA | National Zoning Atlas | https://www.zoningatlas.org/massachusetts
Bowditch — Dover Amendment Case Law | Bowditch LLP | https://www.bowditch.com/bowditchrealestateblog/2024/04/22/prohibiting-non-accessory-bess-violates-massachusetts-law/