METHODOLOGY NOTE Did the CAPEX and MW Capacity Figures Come from the BESS Tool? A detailed account of what the tool produced, what was estimated externally, and what that means for the project. Monzia Moodie, Regulatory & Policy Systems Analyst · Kadir Farah, Storage Systems & Development Specialist Advisor: Marcus Anum · Sponsor: Ledum Nordee · TPS × MassDOER Fellowship · April 2026

|  | SHORT ANSWER No. The CAPEX figures and MW capacity sizes in the presentation were not direct outputs of the BESS siting tool. They were derived separately from published benchmarks and applied as manual estimates on top of the tool’s scoring outputs. The full accounting follows below. |
| --- | --- |

1.  Where the CAPEX Numbers Came From

The CAPEX figures were calculated using a straightforward formula applied outside the tool:

Gross CAPEX = Modeled MWh Capacity × NREL 2024 Installed Cost Benchmark

The NREL 2024 Q1 benchmark used was  $334/kWh  for a 4-hour utility-scale LFP system, sourced from:

- NREL 2025 Battery Storage Cost Projections Update — DOI: 10.2172/2583471

- NREL 2024 Annual Technology Baseline (ATB) — atb.nrel.gov/electricity/2024/utility-scale_battery_storage

Applied to the two modeled project sites:

| Site | Duration | MWh Capacity | Cost Rate | Gross CAPEX |
| --- | --- | --- | --- | --- |
| 231 Beacham St, Everett | 8 hr | 800 MWh | $334/kWh | $267M |
| 283 Eastern Ave, Chelsea | 4 hr | 120 MWh | $334/kWh | ~$40M |

The net CAPEX figures (at 30% and 50% ITC) were then calculated by applying the ITC percentages that the tool’s EJ and physical feasibility layers confirmed as applicable:

- 30% ITC: Prevailing Wage & Apprenticeship base rate (Section 48E, OBBBA July 2025)

- 50% ITC: PWA (30%) + Energy Community bonus (+10%) for brownfield/former industrial sites

- Up to 70% ITC when Low-Income Community bonus (+10–20%) is added for EJ-designated census tracts

|  | IMPORTANT LIMITATION The $334/kWh benchmark is for a 4-hour system. An 8-hour system carries a different cost profile — the higher energy-to-power ratio typically reduces per-kWh cost for longer durations, but NREL’s ATB does not provide a distinct 8hr benchmark at this specificity. The same $334/kWh figure was applied to Everett’s 8hr system, which slightly overstates gross CAPEX. A more precise model would use duration-adjusted cost curves from NREL’s full scenario library. |
| --- | --- |

The tool itself identified that both sites qualify for the energy community and low-income community ITC bonuses through its Layer 1 (EJ & Regulatory) and Layer 4 (Physical Feasibility) outputs. But the CAPEX arithmetic — multiplying MWh by $/kWh and then applying ITC percentages — was performed outside the tool using those flags as inputs.

2.  Where the MW/MWh Capacity Figures Came From

This is where the most important distinction lies. The tool’s Physical Feasibility layer (Layer 4) does produce a maximum feasible MW estimate — using this logic:

Net Buildable Area (sq ft, after setbacks) × Power Density (kW/sq ft for containerized LFP) = Maximum MW

For the Everett municipality overall, the tool assigned a Physical Feasibility score of 24/25, consistent with a large industrial brownfield parcel. For Chelsea overall, it assigned 21/25, consistent with a constrained urban industrial parcel.

|  | CRITICAL DISTINCTION The tool in its current form scores municipalities, not individual parcels. The specific capacity figures used in the presentation (200 MW for 231 Beacham Street, 30 MW for 283 Eastern Avenue) were parcel-level estimates applied on top of the tool’s municipal scoring — they were not direct tool outputs. |
| --- | --- |

231 Beacham Street, Everett — 200 MW / 800 MWh (8hr)

The following assumptions were applied:

- Assumed approximately 5 acres of net buildable area (estimated for an industrial parcel in the Beacham Street industrial corridor, after applying the 50 ft setback rule confirmed by the tool’s Layer 3 output)

- Applied a typical containerized BESS power density of approximately 40 MW per acre for utility-scale LFP systems

- 5 acres × 40 MW/acre = 200 MW modeled capacity

- Duration (8hr): Selected by the tool’s Layer 5 revenue optimization — 8hr maximizes FCM capacity payments and 83E long-duration contract eligibility in the SENE zone

|  | VERIFICATION NOTE The actual parcel size at 231 Beacham Street was not independently verified through GIS analysis or county parcel records. The ~5 acre estimate is a reasonable approximation for the industrial corridor, but it has not been confirmed by parcel-level data. |
| --- | --- |

283 Eastern Avenue, Chelsea — 30 MW / 120 MWh (4hr)

The following assumptions were applied:

- Assumed approximately 3 acres of net buildable area for an urban I-1/I-2 industrial parcel in the Eastern Avenue corridor, after the 50 ft setback rule (confirmed by Layer 3)

- Applied a reduced urban density factor of approximately 10 MW per acre (vs. 40 MW/acre for Everett) to account for urban site access constraints and building clearance requirements

- ~3 acres × 10 MW/acre = 30 MW modeled capacity

- Duration (4hr): Tool’s Layer 5 revenue optimization for the SENE zone at this scale — 4hr maximizes CPS multiplier eligibility and SMART adder qualification

|  | VERIFICATION NOTE The actual parcel dimensions at 283 Eastern Avenue were also not independently verified through GIS analysis or parcel records. The ~3 acre estimate is based on the Eastern Avenue industrial corridor profile, not confirmed site data. |
| --- | --- |

3.  What the Tool Produced vs. What Was Added Externally

The following table provides a precise, line-by-line accounting of which outputs in the presentation came directly from the BESS siting tool and which were calculated or estimated externally.

| Output / Data Point | From the BESS Tool? | Source |
| --- | --- | --- |
| Municipality composite score (119/125, 113/125) | YES — Direct Tool Output | Five-layer MCE scoring across all 13 municipalities |
| EJ designation status, CIA severity rating | YES — Direct Tool Output | Layer 1: MassGIS OEJE 2020 EJ Population Layer + CIA 33-indicator framework |
| Hosting capacity rating (Very High, High) | YES — Direct Tool Output | Layer 2: Eversource Hosting Capacity Map / National Grid SDP |
| Interconnection risk level (Very Low, Low) | YES — Direct Tool Output | Layer 2: Substation proximity + circuit headroom analysis |
| Zoning class, setback distance, permitting path | YES — Direct Tool Output | Layer 3: DOER Model Bylaw tiers + municipal zoning codes |
| Physical feasibility score (24/25, 21/25) | YES — Direct Tool Output | Layer 4: Parcel-level brownfield/industrial site assessment |
| Max feasible MW range (municipal level) | PARTIAL — Tool produces a range | Layer 4 outputs a range; specific parcel-scale figures were estimated externally |
| Optimal duration (8hr for Everett, 4hr for Chelsea) | YES — Direct Tool Output | Layer 5: Revenue optimization across FCM, CPS, SMART, and arbitrage for SENE zone |
| Revenue score and $/kW-yr range ($90–$170+) | YES — Direct Tool Output | Layer 5: ISO-NE NEMA/SENE LMP, FCA clearing prices, CPS ACP schedule, SMART adder |
| ITC bonus tier eligibility flags | YES — Direct Tool Output | Layers 1 + 4 combined: EJ census tract status + brownfield/industrial designation |
| Specific MW/MWh capacity (200 MW, 30 MW) | NO — External Estimate | Assumed parcel acreage × power density factor (not GIS-confirmed) |
| Gross CAPEX ($267M, $40M) | NO — External Calculation | NREL 2024 $334/kWh × modeled MWh capacity |
| Net CAPEX (at 30% and 50% ITC) | NO — External Calculation | Gross CAPEX × (1 − ITC%) using tool-confirmed ITC eligibility flags |
| NPV and IRR | NO — External Financial Model | 20-year DCF model built externally using tool outputs as inputs; 8% WACC; NREL O&M rates |

4.  What This Means for the Presentation and the Project

The financial slides and site profile slides are tool-informed but not tool-generated for the CAPEX and capacity line items. The five-layer municipal scoring and site selection are fully tool-derived. The economics shown in the financial comparison slide are a downstream model that uses the tool’s outputs — EJ eligibility, hosting capacity, zoning, revenue stack, ITC flags — as inputs into a separate financial calculation using NREL costs and ISO-NE revenue data.

In presentation terms, this means:

- The tool’s claim to identify the best sites (Everett #1, Chelsea #2) is fully defensible and directly supported by the five-layer MCE scoring

- The financial figures shown are reasonable, benchmark-grounded estimates — but should be introduced to audiences as “tool-informed financial modeling” rather than “tool outputs”

- Speaker notes or footnotes on the financial comparison slide should clarify that CAPEX and MW figures are modeled estimates pending GIS-confirmed parcel-level data

Recommended Next Development Step

To make the CAPEX and capacity figures genuinely tool-generated, a sixth output module should be added to the tool with the following logic:

| Step | Action | Data Source |
| --- | --- | --- |
| 1 | Accept a specific parcel address and GIS-confirmed acreage as inputs | County parcel records, MassGIS parcel layer |
| 2 | Apply municipality-specific setback rules (already in Layer 3) to calculate net buildable area | DOER Model Bylaw + municipal zoning codes |
| 3 | Apply configurable power density factor to produce parcel-specific MW estimate | Industry standard: 20–50 MW/acre for containerized LFP |
| 4 | Multiply by NREL cost curve (already in Layer 5) to produce a CAPEX range | NREL ATB 2024/2025 with duration adjustment |
| 5 | Apply confirmed ITC tiers (Layers 1+4 flags) to produce net CAPEX scenarios | OBBBA July 2025 Section 48E ITC schedule |
| 6 | Output full pro forma (Revenue, O&M, EBITDA, NPV, IRR) as a tool deliverable | Layer 5 revenue stack + NREL O&M benchmark |

Adding this module would close the gap between what the tool currently does and what the financial slides imply it does — making the investment narrative fully defensible end-to-end.

5.  Data Sources Referenced in This Note

| Source | Organization | URL / Reference |
| --- | --- | --- |
| NREL 2025 Battery Storage Cost Projections Update | NREL | DOI: 10.2172/2583471 · docs.nrel.gov/docs/fy25osti/93281.pdf |
| NREL 2024 Annual Technology Baseline (ATB) | NREL | atb.nrel.gov/electricity/2024/utility-scale_battery_storage |
| ISO-NE Forward Capacity Auction Results (FCA 14–18) | ISO-NE / ISO Newswire | isonewswire.com |
| ISO-NE 2024 Annual Markets Report | ISO-NE | iso-ne.com/static-assets/documents/100023/2024-annual-markets-report.pdf |
| MassGIS 2020 EJ Population Layer | MassGIS / OEJE | mass.gov/info-details/massgis-data-2020-environmental-justice-populations |
| OEJE CIA Standards & Guidelines (980 CMR 15.00) | OEJE | Issued January 23, 2026 |
| DOER Model BESS Bylaw | MassDOER | mass.gov/doc/doer-draft-battery-energy-storage-systems-bess-model-bylaw/download (Oct 6, 2025) |
| One Big Beautiful Bill Act — Section 48E ITC | US Congress | Enacted July 2025 |
| Eversource Hosting Capacity Map | Eversource / envelio | eversource.com/residential/about/doing-business-with-us/interconnections/massachusetts/hosting-capacity-map |

This document is a methodology note prepared for internal project review. All financial figures are tool-informed estimates based on publicly available benchmark data. They do not constitute a formal financial analysis, appraisal, or investment advice. Parcel-specific capacity and CAPEX figures should be verified against GIS-confirmed site data before use in formal project financing or regulatory submissions.